## INFO
Regional Adequacy Assessment results
Week: | 8
Period start: | 15.02.2020
Period end: | 21.02.2020
Problematic hour: | 105
Used UCTE CGM: | 20200212_0830_FO3_UX0.UCT
Comments: | HU was not included in calculation due to some tool issues. For 6 hours, marked with "0" on sheet "X", RAA optimization could not be performed, since TIC is bigger than Available capacity of the region. Critical hour in Week08 is 105 hour, 9th form Wednesday 19.02.2020. PTDF calculations are simulated on CGM for 9th hour of past Wednesday (12.02.2020). Load flow inconsistencies (e.g. sum of imports for RS is not equal to the negative ERIC value of RS) detected in previous calculations are finally solved - initially prediction that load flow losses create problem are rejected (since DC load flow is used for PTDF calculation, where losses are neglected and do not exist). After analysis of PTDF results, it is concluded that there was problem with distribution of production in Generation Shift Key (GSK) list, which is an input file for PTDF calculation and is defined based on percent distribution of negative ERIC values of Areas that are part of the HUB. After incuding 2 decimal places in distribution coeficients, all problems with PTDF calculations are solved.
Explanation of document: | RAA results for defined timestamp are organized in several sheets: - ERIC sheet contains following data: ERIC (Expected Remaining/Insufficient Capacity) values - these valus give the expected amount of capacity that is available for export(positive sign)/import(negative sign) ensuring that the system will stay/become adequate, SAIT (System Adequacy Index Target) values - the optimum trade-off between grid investments and potential losses from unserved energy representing the desired level of adequacy defined by each TSO or NRA, - H sheet contains data that explain how critical hour (H) was defined, - X sheet contains following data: HUB - areas with negative ERIC value for defined timestamp (these are importing areas in the PTDF calculation process), TIC (Total Insufficient Capacity) - the absolute value of the region's total expected insufficient capacity, TIF (Total Increase of active power Flow) - total change of active power flows across all observed tie-lines in the region, X (adequacy transactions) - potential transactions from specific area with positive ERIC value to HUB area, required for solving the adequacy issue in a way that active power flows across all network elements of the observed region are minimally altered, - dF sheet contains following data: ∆F - the change of active load flow on specific tie-line, oriented in defined direction - MAP sheet contains following data: border flows, negative ERIC values for areas in HUB and positive X values for areas that are solving adequacy issue.

## ERIC
| SAIT | 0.99726 | 0.99726 | 0.99726 | 0.99726 | 0.99726 | 1 | 0.99726 | 0.99726 | 0.99726 | 0.99726 | 0.99726
Date | Hour\Area | AL | BA | BG | GR | HR | HU | ME | MK | RO | RS | SI
2020-02-15 | 1 | 550 | 1730 | 1731 | 2584 | 595 | 0 | 52 | -68 | 1267 | 440 | -506
| 2 | 550 | 1441 | 1852 | 2804 | 729 | 0 | 86 | 19 | 1355 | 744 | -473
| 3 | 550 | 1475 | 1898 | 3095 | 795 | 0 | 117 | 87 | 1422 | 934 | -426
| 4 | 550 | 1466 | 1885 | 3260 | 810 | 0 | 132 | 136 | 1477 | 1022 | -425
| 5 | 550 | 1416 | 1837 | 3297 | 779 | 0 | 138 | 136 | 1488 | 917 | -425
| 6 | 550 | 1296 | 1639 | 3170 | 629 | 0 | 130 | 110 | 1224 | 671 | -433
| 7 | 550 | 981 | 1279 | 3038 | 254 | 0 | 109 | 32 | 1201 | 364 | -513
| 8 | 550 | 781 | 751 | 2923 | -1 | 0 | 69 | -18 | 1033 | 52 | -334
| 9 | 550 | 691 | 895 | 3039 | -131 | 0 | 20 | -80 | 898 | -174 | -421
| 10 | 550 | 669 | 1141 | 3244 | -155 | 0 | -10 | -121 | 900 | -205 | -445
| 11 | 550 | 693 | 1385 | 3334 | -93 | 0 | -15 | -108 | 978 | -188 | -446
| 12 | 550 | 655 | 1279 | 3417 | -94 | 0 | -8 | -68 | 834 | -126 | -420
| 13 | 550 | 660 | 1462 | 3630 | -47 | 0 | -3 | -28 | 847 | -55 | -384
| 14 | 550 | 712 | 1514 | 3378 | 26 | 0 | 5 | -6 | 703 | 2634 | -291
| 15 | 550 | 775 | 1454 | 3160 | 87 | 0 | 6 | -80 | 665 | 73 | -262
| 16 | 550 | 812 | 1145 | 2846 | 117 | 0 | -4 | -71 | 517 | 4 | -255
| 17 | 550 | 750 | 770 | 2108 | 65 | 0 | -20 | -28 | 78 | -286 | -281
| 18 | 550 | 624 | 661 | 1720 | -138 | 0 | -60 | -94 | 117 | -331 | -433
| 19 | 550 | 537 | 709 | 1917 | -266 | 0 | -72 | -116 | -19 | -302 | -511
| 20 | 550 | 498 | 963 | 2324 | -286 | 0 | -70 | -115 | 35 | -205 | -492
| 21 | 550 | 579 | 1249 | 2826 | -209 | 0 | -62 | -86 | 353 | -61 | -447
| 22 | 550 | 688 | 1113 | 3179 | -158 | 0 | -50 | -58 | 710 | -47 | -352
| 23 | 550 | 846 | 1394 | 3676 | 36 | 0 | -33 | -156 | 1337 | -55 | -344
| 24 | 550 | 1067 | 1669 | 4083 | 292 | 0 | -22 | -93 | 1266 | -34 | -253
2020-02-16 | 1 | 701 | 1330 | 1879 | 4117 | 532 | 0 | 6 | -35 | 1371 | 245 | -347
| 2 | 701 | 1454 | 1972 | 4309 | 678 | 0 | 42 | 61 | 1473 | 582 | -315
| 3 | 701 | 1523 | 2036 | 4446 | 749 | 0 | 72 | 132 | 1478 | 817 | -285
| 4 | 701 | 1550 | 2045 | 4433 | 766 | 0 | 90 | 178 | 1446 | 963 | -291
| 5 | 701 | 1546 | 1962 | 4259 | 737 | 0 | 97 | 178 | 1421 | 979 | -300
| 6 | 701 | 1492 | 1819 | 4092 | 594 | 0 | 92 | 140 | 1425 | 863 | -322
| 7 | 701 | 1392 | 1499 | 3970 | 240 | 0 | 76 | 59 | 1376 | 713 | -393
| 8 | 701 | 1314 | 956 | 3885 | 0 | 0 | 44 | -17 | 1128 | 459 | -230
| 9 | 701 | 1177 | 1058 | 3786 | -118 | 0 | -1 | -68 | 1055 | 206 | -326
| 10 | 701 | 1048 | 1171 | 3605 | -139 | 0 | -39 | -110 | 1243 | 394 | -365
| 11 | 701 | 952 | 1408 | 3535 | -87 | 0 | -55 | -102 | 1269 | 101 | -348
| 12 | 701 | 896 | 1264 | 3641 | -98 | 0 | -54 | -67 | 1128 | 198 | -337
| 13 | 701 | 933 | 1506 | 3951 | -65 | 0 | -43 | -28 | 984 | 316 | -301
| 14 | 701 | 1031 | 1618 | 3688 | 1 | 0 | -31 | -7 | 1046 | 3020 | -228
| 15 | 701 | 1128 | 1512 | 3393 | 60 | 0 | -32 | -87 | 1056 | 431 | -190
| 16 | 701 | 1172 | 1191 | 3027 | 97 | 0 | -35 | -79 | 815 | 380 | -209
| 17 | 701 | 1121 | 656 | 2217 | 50 | 0 | -44 | -31 | 602 | 112 | -244
| 18 | 701 | 973 | 428 | 1737 | -153 | 0 | -77 | -92 | 419 | 83 | -377
| 19 | 701 | 870 | 407 | 1689 | -279 | 0 | -88 | -109 | 400 | 101 | -452
| 20 | 701 | 817 | 626 | 1979 | -302 | 0 | -89 | -104 | 555 | 147 | -491
| 21 | 701 | 863 | 959 | 2425 | -225 | 0 | -87 | -71 | 723 | 268 | -451
| 22 | 701 | 936 | 902 | 2835 | -174 | 0 | -81 | -45 | 1103 | 261 | -319
| 23 | 701 | 1034 | 1356 | 3477 | 19 | 0 | -63 | -125 | 1565 | 302 | -299
| 24 | 701 | 1218 | 1699 | 3941 | 276 | 0 | -27 | -85 | 1603 | 456 | -208
2020-02-17 | 1 | 711 | 1404 | 1838 | 3959 | 517 | 0 | 26 | -44 | 1624 | 688 | -329
| 2 | 711 | 1511 | 1933 | 4113 | 661 | 0 | 63 | 45 | 1702 | 998 | -304
| 3 | 711 | 1561 | 1974 | 4179 | 733 | 0 | 84 | 112 | 1761 | 1209 | -292
| 4 | 711 | 1570 | 1889 | 4032 | 753 | 0 | 99 | 158 | 1759 | 1288 | -295
| 5 | 711 | 1536 | 1643 | 3472 | 727 | 0 | 103 | 170 | 1627 | 1092 | -337
| 6 | 711 | 1396 | 1027 | 2659 | 585 | 0 | 92 | 138 | 953 | 594 | -474
| 7 | 711 | 1054 | 455 | 2491 | 232 | 0 | 41 | 62 | 182 | 147 | -640
| 8 | 711 | 838 | 171 | 2552 | -7 | 0 | -16 | -5 | -201 | -85 | -660
| 9 | 711 | 732 | 552 | 2814 | -125 | 0 | -47 | -73 | -321 | -205 | -670
| 10 | 711 | 705 | 865 | 3008 | -143 | 0 | -61 | -100 | -144 | -162 | -632
| 11 | 711 | 726 | 1164 | 3075 | -95 | 0 | -62 | -112 | 256 | -166 | -598
| 12 | 711 | 682 | 1145 | 3076 | -108 | 0 | -55 | -36 | 336 | -144 | -534
| 13 | 711 | 687 | 1207 | 3072 | -71 | 0 | -48 | 7 | 294 | -117 | -566
| 14 | 711 | 730 | 1153 | 2664 | -4 | 0 | -36 | 27 | 450 | 2810 | -571
| 15 | 711 | 786 | 1005 | 2265 | 59 | 0 | -31 | -56 | 371 | -45 | -548
| 16 | 711 | 823 | 895 | 1810 | 96 | 0 | -30 | -50 | 338 | -124 | -539
| 17 | 711 | 761 | 592 | 991 | 51 | 0 | -41 | -1 | 135 | -426 | -602
| 18 | 711 | 635 | 313 | 478 | -157 | 0 | -79 | -65 | -86 | -446 | -650
| 19 | 711 | 550 | 272 | 421 | -283 | 0 | -86 | -93 | -110 | -392 | -700
| 20 | 711 | 512 | 526 | 794 | -308 | 0 | -80 | -126 | -196 | -274 | -684
| 21 | 711 | 594 | 859 | 1396 | -232 | 0 | -75 | -92 | 249 | -122 | -566
| 22 | 711 | 708 | 795 | 1780 | -182 | 0 | -61 | -67 | 959 | -136 | -430
| 23 | 711 | 872 | 1208 | 2396 | 12 | 0 | -45 | -113 | 1319 | -109 | -434
| 24 | 711 | 1094 | 1713 | 2829 | 269 | 0 | -41 | -96 | 1534 | -82 | -323
2020-02-18 | 1 | 681 | 1316 | 1793 | 2814 | 508 | 0 | -13 | -30 | 1468 | 222 | -455
| 2 | 681 | 1436 | 1879 | 2939 | 652 | 0 | 34 | 62 | 1542 | 525 | -347
| 3 | 681 | 1490 | 1905 | 2999 | 726 | 0 | 56 | 134 | 1590 | 765 | -338
| 4 | 681 | 1500 | 1857 | 2851 | 746 | 0 | 80 | 183 | 1395 | 810 | -373
| 5 | 681 | 1471 | 1691 | 2325 | 719 | 0 | 89 | 181 | 1150 | 642 | -413
| 6 | 681 | 1342 | 1198 | 1536 | 577 | 0 | 79 | 138 | 650 | 207 | -534
| 7 | 681 | 1018 | 662 | 1367 | 223 | 0 | 28 | 42 | 100 | -171 | -849
| 8 | 681 | 814 | 305 | 1441 | 19 | 0 | -13 | -33 | -271 | -333 | -680
| 9 | 681 | 723 | 596 | 1700 | -105 | 0 | -45 | -99 | -235 | -386 | -669
| 10 | 681 | 704 | 908 | 1900 | -127 | 0 | -63 | -135 | 9 | -330 | -609
| 11 | 681 | 726 | 1152 | 2002 | -93 | 0 | -71 | -119 | -40 | -246 | -623
| 12 | 681 | 688 | 1147 | 2055 | -111 | 0 | -69 | -72 | -304 | -155 | -586
| 13 | 681 | 697 | 1212 | 2131 | -78 | 0 | -73 | -18 | -450 | -68 | -570
| 14 | 681 | 740 | 1234 | 1798 | -5 | 0 | -66 | 6 | -380 | 2822 | -559
| 15 | 681 | 796 | 1111 | 1467 | 61 | 0 | -51 | -78 | -443 | -39 | -512
| 16 | 681 | 831 | 886 | 1013 | 101 | 0 | -45 | -71 | -505 | -124 | -487
| 17 | 681 | 769 | 561 | 200 | 64 | 0 | -49 | -22 | -648 | -468 | -524
| 18 | 681 | 643 | 302 | -262 | -125 | 0 | -76 | -82 | -759 | -525 | -632
| 19 | 681 | 557 | 265 | -294 | -295 | 0 | -81 | -110 | -834 | -496 | -700
| 20 | 681 | 517 | 566 | 179 | -331 | 0 | -88 | -117 | -716 | -402 | -721
| 21 | 681 | 596 | 869 | 835 | -255 | 0 | -92 | -84 | -309 | -246 | -627
| 22 | 681 | 708 | 801 | 1280 | -205 | 0 | -78 | -57 | 254 | -226 | -437
| 23 | 681 | 870 | 1199 | 1969 | -4 | 0 | -61 | -144 | 653 | -170 | -515
| 24 | 681 | 1091 | 1560 | 2489 | 259 | 0 | -50 | -96 | 825 | -96 | -359
2020-02-19 | 1 | 670 | 1312 | 1754 | 2544 | 503 | 0 | -29 | -62 | 977 | 219 | -575
| 2 | 670 | 1430 | 1852 | 2715 | 650 | 0 | 26 | 28 | 1017 | 515 | -539
| 3 | 670 | 1483 | 1895 | 2817 | 724 | 0 | 49 | 99 | 1044 | 752 | -533
| 4 | 670 | 1490 | 1857 | 2716 | 742 | 0 | 75 | 149 | 973 | 790 | -540
| 5 | 670 | 1461 | 1700 | 2236 | 712 | 0 | 73 | 150 | 782 | 601 | -573
| 6 | 670 | 1331 | 1214 | 1439 | 569 | 0 | 73 | 108 | 215 | 128 | -686
| 7 | 670 | 1006 | 682 | 1214 | 224 | 0 | 44 | 18 | -330 | -287 | -1023
| 8 | 670 | 802 | 321 | 1181 | -12 | 0 | -31 | -49 | -831 | -470 | -857
| 9 | 670 | 711 | 589 | 1378 | -114 | 0 | -70 | -113 | -938 | -522 | -839
| 10 | 670 | 693 | 889 | 1541 | -109 | 0 | -92 | -137 | -769 | -455 | -787
| 11 | 670 | 718 | 1133 | 1616 | -37 | 0 | -87 | -108 | -503 | -367 | -803
| 12 | 670 | 678 | 1131 | 1618 | -36 | 0 | -79 | -58 | -483 | -274 | -755
| 13 | 670 | 687 | 1202 | 1634 | 8 | 0 | -79 | -5 | -516 | -185 | -752
| 14 | 670 | 733 | 1231 | 1319 | 80 | 0 | -71 | 24 | -375 | 2729 | -703
| 15 | 670 | 790 | 1110 | 1125 | 137 | 0 | -71 | -68 | -440 | -115 | -679
| 16 | 670 | 827 | 886 | 875 | 158 | 0 | -73 | -62 | -614 | -182 | -666
| 17 | 670 | 766 | 561 | 168 | 101 | 0 | -80 | -4 | -744 | -511 | -665
| 18 | 670 | 639 | 304 | -281 | -102 | 0 | -104 | -67 | -916 | -552 | -775
| 19 | 670 | 553 | 267 | -253 | -276 | 0 | -113 | -101 | -873 | -504 | -843
| 20 | 670 | 511 | 567 | 193 | -304 | 0 | -110 | -108 | -742 | -394 | -851
| 21 | 670 | 591 | 869 | 894 | -217 | 0 | -98 | -73 | -367 | -229 | -759
| 22 | 670 | 699 | 789 | 1341 | -160 | 0 | -81 | -40 | 149 | -199 | -607
| 23 | 670 | 860 | 1188 | 2065 | 12 | 0 | -62 | -137 | 640 | -133 | -673
| 24 | 670 | 1078 | 1559 | 2575 | 251 | 0 | -58 | -92 | 1041 | -48 | -565
2020-02-20 | 1 | 660 | 1298 | 1723 | 2614 | 475 | 0 | -29 | -72 | 1088 | 273 | -494
| 2 | 660 | 1416 | 1824 | 2766 | 632 | 0 | 21 | 17 | 1208 | 597 | -470
| 3 | 660 | 1468 | 1858 | 2852 | 713 | 0 | 45 | 88 | 1243 | 851 | -452
| 4 | 660 | 1476 | 1814 | 2724 | 747 | 0 | 63 | 140 | 1198 | 906 | -458
| 5 | 660 | 1445 | 1658 | 2238 | 743 | 0 | 85 | 144 | 1077 | 726 | -453
| 6 | 660 | 1315 | 1175 | 1440 | 669 | 0 | 95 | 105 | 481 | 256 | -609
| 7 | 660 | 990 | 646 | 1158 | 509 | 0 | 47 | 23 | -83 | -157 | -941
| 8 | 660 | 794 | 285 | 1064 | 360 | 0 | -10 | -51 | -433 | -336 | -747
| 9 | 660 | 703 | 566 | 1233 | 168 | 0 | -54 | -115 | -662 | -382 | -737
| 10 | 660 | 689 | 875 | 1408 | 85 | 0 | -84 | -146 | -538 | -314 | -652
| 11 | 660 | 705 | 1126 | 1523 | 93 | 0 | -89 | -120 | -296 | -225 | -645
| 12 | 660 | 661 | 1130 | 1666 | 112 | 0 | -69 | -71 | -363 | -134 | -607
| 13 | 660 | 662 | 1200 | 1868 | 181 | 0 | -62 | -12 | -407 | -46 | -599
| 14 | 660 | 704 | 1226 | 1682 | 292 | 0 | -59 | 19 | -240 | 2879 | -546
| 15 | 660 | 755 | 1108 | 1637 | 398 | 0 | -46 | -53 | -24 | -6 | -537
| 16 | 660 | 785 | 885 | 1484 | 432 | 0 | -39 | -48 | 117 | -91 | -528
| 17 | 660 | 705 | 562 | 765 | 384 | 0 | -52 | -5 | -78 | -441 | -566
| 18 | 660 | 569 | 302 | 313 | 182 | 0 | -96 | -83 | -296 | -496 | -631
| 19 | 660 | 516 | 269 | 366 | -31 | 0 | -106 | -114 | -166 | -461 | -727
| 20 | 660 | 499 | 574 | 888 | -76 | 0 | -103 | -123 | -21 | -362 | -702
| 21 | 660 | 574 | 878 | 1598 | -29 | 0 | -99 | -92 | 433 | -210 | -599
| 22 | 660 | 665 | 803 | 2059 | 9 | 0 | -82 | -58 | 1049 | -194 | -465
| 23 | 660 | 828 | 1200 | 2743 | 157 | 0 | -64 | -138 | 1504 | -142 | -493
| 24 | 660 | 1050 | 1574 | 3286 | 393 | 0 | -39 | -85 | 1693 | -98 | -397
2020-02-21 | 1 | 659 | 1264 | 1693 | 3359 | 592 | 0 | 15 | -66 | 1692 | -336 | -549
| 2 | 659 | 1381 | 1783 | 3548 | 745 | 0 | 64 | 28 | 1898 | 8 | -515
| 3 | 659 | 1434 | 1819 | 3671 | 829 | 0 | 91 | 102 | 2019 | 333 | -488
| 4 | 659 | 1445 | 1777 | 3583 | 875 | 0 | 111 | 160 | 2194 | 589 | -505
| 5 | 659 | 1415 | 1614 | 3128 | 884 | 0 | 118 | 164 | 1824 | 636 | -542
| 6 | 659 | 1287 | 1115 | 2369 | 833 | 0 | 103 | 130 | 1366 | 452 | -691
| 7 | 659 | 970 | 569 | 2150 | 749 | 0 | 52 | 48 | 957 | -28 | -1019
| 8 | 659 | 767 | 202 | 2117 | 658 | 0 | -17 | -38 | 832 | -454 | -830
| 9 | 659 | 680 | 473 | 2344 | 476 | 0 | -59 | -99 | 753 | -648 | -837
| 10 | 659 | 663 | 776 | 2538 | 325 | 0 | -73 | -126 | 691 | -711 | -763
| 11 | 659 | 680 | 1024 | 2655 | 236 | 0 | -69 | -98 | 1147 | -654 | -723
| 12 | 659 | 633 | 1028 | 2742 | 224 | 0 | -63 | -41 | 1309 | -567 | -682
| 13 | 659 | 626 | 1093 | 2857 | 321 | 0 | -52 | 20 | 1255 | -474 | -635
| 14 | 659 | 660 | 1122 | 2584 | 467 | 0 | -41 | 47 | 1250 | -384 | -599
| 15 | 659 | 727 | 1011 | 2421 | 589 | 0 | -30 | -29 | 1323 | 2628 | -558
| 16 | 659 | 762 | 780 | 2176 | 643 | 0 | -31 | -26 | 1175 | -329 | -505
| 17 | 659 | 692 | 443 | 1405 | 610 | 0 | -42 | 22 | 735 | -409 | -591
| 18 | 659 | 585 | 171 | 865 | 401 | 0 | -80 | -51 | 577 | -763 | -662
| 19 | 659 | 505 | 131 | 930 | 166 | 0 | -93 | -89 | 464 | -825 | -726
| 20 | 659 | 497 | 439 | 1386 | 74 | 0 | -93 | -95 | 361 | -793 | -701
| 21 | 659 | 579 | 749 | 1979 | 68 | 0 | -85 | -61 | 711 | -694 | -652
| 22 | 659 | 680 | 674 | 2321 | 82 | 0 | -64 | -26 | 1216 | -527 | -492
| 23 | 659 | 817 | 1082 | 2867 | 224 | 0 | -42 | -110 | 1925 | -502 | -519
| 24 | 659 | 1021 | 1471 | 3321 | 484 | 0 | -25 | -56 | 1925 | -442 | -443

## H
Hour in Week | Hour in day | Areas in HUB | TIC for day [MW] | Available capacity [MW] | Opmisation possible? (0=No, 1=Yes)
115 | 19 | 7 | -2963 | 1490 | 0
91 | 19 | 7 | -2810 | 1503 | 0
114 | 18 | 7 | -2797 | 1613 | 0
105 | 9 | 6 | -2596 | 3348 | 1
116 | 20 | 6 | -2509 | 1941 | 0
90 | 18 | 7 | -2461 | 1626 | 0
92 | 20 | 6 | -2375 | 1943 | 0
106 | 10 | 6 | -2349 | 3793 | 1
104 | 8 | 6 | -2250 | 2974 | 1
113 | 17 | 5 | -2004 | 2266 | 1
129 | 9 | 5 | -1950 | 3330 | 1
107 | 11 | 6 | -1905 | 4137 | 1
117 | 21 | 6 | -1743 | 3024 | 1
130 | 10 | 5 | -1734 | 3717 | 1
163 | 19 | 4 | -1733 | 2855 | 1
89 | 17 | 5 | -1711 | 2275 | 1
108 | 12 | 6 | -1685 | 4097 | 1
164 | 20 | 4 | -1682 | 3416 | 1
154 | 10 | 4 | -1673 | 5652 | 1
68 | 20 | 6 | -1668 | 2543 | 1
67 | 19 | 6 | -1664 | 1954 | 1
153 | 9 | 4 | -1643 | 5385 | 1
103 | 7 | 3 | -1640 | 3858 | 1
93 | 21 | 6 | -1613 | 2981 | 1
139 | 19 | 6 | -1605 | 1811 | 1
138 | 18 | 5 | -1602 | 2026 | 1
112 | 16 | 5 | -1597 | 3416 | 1
128 | 8 | 5 | -1577 | 3163 | 1
162 | 18 | 4 | -1556 | 3258 | 1
155 | 11 | 4 | -1544 | 6401 | 1
81 | 9 | 6 | -1539 | 3700 | 1
109 | 13 | 5 | -1537 | 4201 | 1
165 | 21 | 4 | -1492 | 4745 | 1
66 | 18 | 6 | -1483 | 2137 | 1
57 | 9 | 6 | -1441 | 4809 | 1
140 | 20 | 6 | -1387 | 2621 | 1
131 | 11 | 5 | -1375 | 4107 | 1
111 | 15 | 5 | -1373 | 3832 | 1
156 | 12 | 4 | -1353 | 6595 | 1
152 | 8 | 4 | -1339 | 5235 | 1
80 | 8 | 5 | -1330 | 3260 | 1
84 | 12 | 6 | -1297 | 4571 | 1
19 | 19 | 6 | -1286 | 3713 | 1
82 | 10 | 5 | -1264 | 4202 | 1
85 | 13 | 6 | -1257 | 4721 | 1
132 | 12 | 5 | -1244 | 4229 | 1
58 | 10 | 6 | -1242 | 5289 | 1
88 | 16 | 5 | -1232 | 3512 | 1
83 | 11 | 6 | -1192 | 4561 | 1
127 | 7 | 3 | -1181 | 4033 | 1
167 | 23 | 4 | -1173 | 7574 | 1
20 | 20 | 5 | -1168 | 4370 | 1
157 | 13 | 3 | -1161 | 6831 | 1
110 | 14 | 3 | -1149 | 6786 | 1
137 | 17 | 5 | -1142 | 3076 | 1
133 | 13 | 5 | -1126 | 4571 | 1
87 | 15 | 5 | -1123 | 4116 | 1
166 | 22 | 4 | -1109 | 5632 | 1
69 | 21 | 5 | -1087 | 3809 | 1
118 | 22 | 5 | -1087 | 3648 | 1
65 | 17 | 4 | -1070 | 3241 | 1
18 | 18 | 5 | -1056 | 3672 | 1
151 | 7 | 2 | -1047 | 6154 | 1
161 | 17 | 3 | -1042 | 4566 | 1
59 | 11 | 5 | -1033 | 5932 | 1
141 | 21 | 5 | -1029 | 4143 | 1
158 | 14 | 3 | -1024 | 6789 | 1
79 | 7 | 2 | -1020 | 4121 | 1
86 | 14 | 4 | -1010 | 7281 | 1
119 | 23 | 4 | -1005 | 5435 | 1
94 | 22 | 5 | -1003 | 3724 | 1
44 | 20 | 4 | -986 | 4825 | 1
56 | 8 | 6 | -974 | 4272 | 1
168 | 0 | 4 | -966 | 8881 | 1
145 | 1 | 3 | -951 | 9274 | 1
10 | 10 | 5 | -936 | 6504 | 1
43 | 19 | 4 | -928 | 4168 | 1
95 | 23 | 5 | -894 | 5372 | 1
160 | 16 | 4 | -891 | 6195 | 1
60 | 12 | 5 | -877 | 5950 | 1
70 | 22 | 5 | -876 | 4953 | 1
21 | 21 | 5 | -865 | 5557 | 1
11 | 11 | 5 | -850 | 6940 | 1
134 | 14 | 3 | -845 | 7462 | 1
143 | 23 | 4 | -837 | 7092 | 1
45 | 21 | 4 | -834 | 5939 | 1
9 | 9 | 4 | -806 | 6093 | 1
61 | 13 | 4 | -802 | 5978 | 1
142 | 22 | 4 | -799 | 5245 | 1
120 | 0 | 4 | -763 | 7174 | 1
64 | 16 | 4 | -743 | 4673 | 1
12 | 12 | 5 | -716 | 6735 | 1
136 | 16 | 4 | -706 | 4363 | 1
71 | 23 | 4 | -701 | 6518 | 1
42 | 18 | 4 | -699 | 4341 | 1
150 | 6 | 1 | -691 | 8314 | 1
102 | 6 | 1 | -686 | 5747 | 1
63 | 15 | 4 | -680 | 5197 | 1
97 | 1 | 3 | -666 | 7979 | 1
135 | 15 | 5 | -666 | 4558 | 1
22 | 22 | 5 | -665 | 6240 | 1
34 | 10 | 4 | -653 | 8162 | 1
55 | 7 | 1 | -640 | 5375 | 1
46 | 22 | 4 | -619 | 6738 | 1
144 | 0 | 4 | -619 | 8656 | 1
159 | 15 | 3 | -617 | 9358 | 1
17 | 17 | 4 | -615 | 4321 | 1
62 | 14 | 3 | -611 | 8545 | 1
126 | 6 | 1 | -609 | 6196 | 1
96 | 0 | 4 | -601 | 6905 | 1
121 | 1 | 3 | -595 | 8131 | 1
35 | 11 | 4 | -592 | 7966 | 1
23 | 23 | 4 | -588 | 7839 | 1
1 | 1 | 2 | -574 | 8949 | 1
101 | 5 | 1 | -573 | 8385 | 1
36 | 12 | 4 | -556 | 7828 | 1
72 | 0 | 4 | -542 | 8150 | 1
149 | 5 | 1 | -542 | 10442 | 1
100 | 4 | 1 | -540 | 9462 | 1
98 | 2 | 1 | -539 | 8903 | 1
78 | 6 | 1 | -534 | 6408 | 1
99 | 3 | 1 | -533 | 9533 | 1
13 | 13 | 5 | -517 | 7149 | 1
146 | 2 | 1 | -515 | 10114 | 1
7 | 7 | 1 | -513 | 7808 | 1
33 | 9 | 4 | -513 | 7983 | 1
148 | 4 | 1 | -505 | 11393 | 1
73 | 1 | 3 | -498 | 8802 | 1
147 | 3 | 1 | -488 | 10957 | 1
47 | 23 | 3 | -487 | 8454 | 1
54 | 6 | 1 | -474 | 8155 | 1
2 | 2 | 1 | -473 | 9580 | 1
122 | 2 | 1 | -470 | 9141 | 1
124 | 4 | 1 | -458 | 9728 | 1
125 | 5 | 1 | -453 | 8776 | 1
123 | 3 | 1 | -452 | 9778 | 1
37 | 13 | 4 | -437 | 8391 | 1
6 | 6 | 1 | -433 | 9419 | 1
3 | 3 | 1 | -426 | 10373 | 1
4 | 4 | 1 | -425 | 10738 | 1
5 | 5 | 1 | -425 | 10558 | 1
77 | 5 | 1 | -413 | 8949 | 1
24 | 0 | 4 | -402 | 8927 | 1
31 | 7 | 1 | -393 | 10026 | 1
25 | 1 | 2 | -382 | 10181 | 1
49 | 1 | 2 | -373 | 10767 | 1
76 | 4 | 1 | -373 | 10103 | 1
8 | 8 | 3 | -353 | 6159 | 1
74 | 2 | 1 | -347 | 9750 | 1
15 | 15 | 2 | -342 | 6770 | 1
75 | 3 | 1 | -338 | 10346 | 1
53 | 5 | 1 | -337 | 11081 | 1
16 | 16 | 3 | -330 | 5991 | 1
40 | 16 | 3 | -323 | 7383 | 1
30 | 6 | 1 | -322 | 11218 | 1
48 | 0 | 3 | -320 | 9894 | 1
41 | 17 | 3 | -319 | 5459 | 1
26 | 2 | 1 | -315 | 11272 | 1
39 | 15 | 3 | -309 | 8281 | 1
50 | 2 | 1 | -304 | 11737 | 1
29 | 5 | 1 | -300 | 11880 | 1
14 | 14 | 2 | -297 | 9522 | 1
52 | 4 | 1 | -295 | 12259 | 1
51 | 3 | 1 | -292 | 12324 | 1
28 | 4 | 1 | -291 | 12172 | 1
27 | 3 | 1 | -285 | 11954 | 1
38 | 14 | 3 | -266 | 11105 | 1
32 | 8 | 2 | -247 | 8487 | 1

## X
HUB: | HR, ME, MK, RO, RS, SI
TIC [MW] | 2596
TIF [MW] | 5653.4667
Transaction direction | X [MW] | ERIC [MW]
AL>HUB | 524.2139 | 670
BA>HUB | 711 | 711
BG>HUB | 589 | 589
GR>HUB | 771.7861 | 1378
HU>HUB | 0 | 0

## dF
Border direction | Border flow [MW] | TIE line name | ΔF[MW]
SIàEU | -239.83 | TIE 220kV Padriciano - Divača | -4.7326
|  | TIE 400kV Redipuglia - Divača | -24.2827
|  | TIE 400kV Maribor - Kainachtal (1) | -86.8359
|  | TIE 400kV Maribor - Kainachtal (2) | -86.8359
|  | TIE 220kV Podlog - Obersielach | -37.1476
SIàHR | -599.2 | TIE 220kV Cirkovice - Žerjavinec | -46.2319
|  | TIE 400kV Krško - Tumbri (1) | -198.8709
|  | TIE 400kV Krško - Tumbri (2) | -198.8709
|  | TIE 220kV Divača - Pehlin | -32.4846
|  | TIE 400kV Divača - Melina | -122.7378
EUàHU | -208.41 | TIE 750kV Zakhidnoukrainska - Szabolcsbáka | 0
|  | TIE 400kV Levice - God | -54.1501
|  | TIE 400kV Gabčikovo - Gyor | 7.5086
|  | TIE 400kV Zurndorf - Gyor | -72.4823
|  | TIE 220kV Neusiedl - Gyor | -13.7829
|  | TIE 220kV Wien Sudost - Gyor | -12.2784
|  | TIE 220kV Mukacheve - Kisvarna | -2.0421
|  | TIE 400kV Mukacheve - Szabolcsbáka | -7.7406
|  | TIE 400kV Zurndorf - Szombathely | -51.8381
|  | TIE 220kV Mukacheve - Tiszalok | -1.6088
ROàHU | 3.86 | TIE 400kV Arad - Sandorfalva | -20.44
|  | TIE 400kV Nadab - Bekescsaba | 24.2961
RSàHU | 115.64 | TIE 400kV Subotica 3 - Sandorfalva | 115.6374
HRàHU | 88.92 | TIE 400kV Ernestinovo - Peks (1) | 0
|  | TIE 400kV Ernestinovo - Peks (2) | 147.9131
|  | TIE 400kV Žerjavinec - Heviz (1) | 0
|  | TIE 400kV Žerjavinec - Heviz (2) | -58.9921
HRàBA | -723.07 | TIE 220kV Zakučac - Mostar 4 | 0
|  | TIE 220kV Sisak - Prijedor | -70.7166
|  | TIE 220kV Đakovo - Gradačac | -27.4824
|  | TIE 400kV Konjsko - Mostar 4 | -251.7707
|  | TIE 220kV Međurić - Prijedor | -57.2385
|  | TIE 220kV Plat - Trebinje | -7.5475
|  | TIE 220kV Đakovo - Tuzla | -33.7151
|  | TIE 400kV Ernestinovo - Ugljevik | -180.0527
|  | TIE 110kV Buško Blato - Livno | -17.1913
|  | TIE 110kV S. Brod - B. Brod | -15.5555
|  | TIE 110kV Opuzen - Čapljina | -2.2203
|  | TIE 110kV Imotski - Grude | -18.2416
|  | TIE 110kV Knin - B. Grahovo | 1.6049
|  | TIE 110kV Gračac - EVP Kulen Vakuf | -12.9661
|  | TIE 110kV Opuzen - Neum | -5.0102
|  | TIE 110kV Ston - Neum | 5.0102
|  | TIE 110kV Županja - Orašje | -13.6452
|  | TIE 110kV Komolac - Trebinje | -9.0048
|  | TIE 110kV Vrgorac - Ljubuški | -7.3275
HRàRS | -79.01 | TIE 400kV Ernestinovo - S. Mitrovica | -79.0105
|  | TIE 110kV Beli Manastir - Apatin | 0
|  | TIE 110kV Nijemci - Šid | 0
BAàME | -188.09 | TIE 220kV Sarajevo 20 - HE Piva | -13.2371
|  | TIE 400kV Trebinje - Lastva | -106.0382
|  | TIE 220kV Trebinje - HE Perućica | -53.7682
|  | TIE 110kV Trebinje - Herceg Novi | -7.0062
|  | TIE 110kV Bileća - Čvor Vilusi (Nikšić) | -8.0387
BAàRS | 176.02 | TIE 400kV Ugljevik - S. Mitrovica | 139.5852
|  | TIE 220kV Višegrad - Vardište | 12.6431
|  | TIE 110kV Zvornik - Mali Zvornik | 12.9539
|  | TIE 110kV Bijeljina 4 (Janja) - Lešnica | 10.8372
RSàME | -122.87 | TIE 400kV Peć 3 - Ribarevine | -4.4228
|  | TIE 220kV Bajina Bašta - Pljevlja 2 | -68.5324
|  | TIE 220kV Požega - Pljevlja 2 | -43.0308
|  | TIE 110kV Potpeć - Pljevlja 1 | -6.8791
MEàAL | -381.05 | TIE 400kV Podgorica 2 - Tirana 2 | -227.6968
|  | TIE 220kV Podgorica 1 - Koplik | -153.3487
BGàRO | 819.18 | TIE 400kV Kozloduy - Tantareni (2) | 0
|  | TIE 400kV Kozloduy - Tantareni (1) | 463.6365
|  | TIE 400kV Varna - Stupina | 181.9849
|  | TIE 400kV Dobrudzha - Rahman | 173.562
ROàEU | 31.42 | TIE 400kV Rosiori - Mukacheve | 31.4176
RSàRO | 154.04 | TIE 400kV HE Đerdap 1 - Portile de Fier | 154.0391
RSàBG | -127.3 | TIE 400kV Niš 2 - Sofia Zapad | -127.3004
MKàBG | 92.45 | TIE 400kV Štip - Ch.Mogila | 92.4492
|  | TIE 110kV Susica - Petrich | 0
|  | TIE 110kV K. Palanka - Skakavitsa | 0
GRàBG | 165.36 | TIE 400kV Thessaloniki - Blagoevgrad | 165.3596
MKàRS | 301.01 | TIE 400kV Štip - Vranje 4 | 162.8085
|  | TIE 400kV Skopje 4 - Uroševac 2 | 138.2014
RSàAL | -143.53 | TIE 220kV Prizren 2 - Fierza | -143.5339
|  | TIE 400kV Koman - Kosovo B | 0
GRàAL | 0.36 | TIE 400kV Kardia - Zemlak | -1.3371e-14
|  | TIE 110kV Mourtos - Bistrica | 0.36435
MKàGR | -506.39 | TIE 400kV Bitola - Meliti | -331.3124
|  | TIE 400kV Dubrovo - Thessaloniki | -175.0734
GRàTR | 99.68 | TIE 400kV N. Santa - Babaeski | 99.6752
BGàTR | -99.68 | TIE 400kV Maritsa Iztok 3 - Hamitabat (1) | -43.4822
|  | TIE 400kV Maritsa Iztok 3 - Hamitabat (2) | -56.195